## Mapping
No. | Category | CSV | Details | Unit | MQTT JSON | Modbus Address | Remarks
1 | General | Date |  |  | Date
2 |  | Time |  |  | Time
3 | Incoming | V(R) | Incoming Phase Voltage (Red) | Volt (V) | V_R | 1002
4 |  | In1(R1) | Incoming 1 Phase Current (Red) | Ampere (A) | In1_R1 | 1014
5 |  | In1(RPF) | Incoming 1 Phase Power Factor (Red) |  | In1_RPF | 1044
6 |  | V(Y) | Incoming Phase Voltage (Yellow) | Volt (V) | V_Y | 1004
7 |  | In1(Y1) | Incoming 1 Phase Current (Yellow) | Ampere (A) | In1_Y1 | 1016
8 |  | In1(YPF) | Incoming 1 Phase Power Factor (Yellow) |  | In1_YPF | 1046
9 |  | V(B) | Incoming Phase Voltage (Blue) | Volt (V) | V_B | 1006
10 |  | In1(B1) | Incoming 1 Phase Current (Blue) | Ampere (A) | In1_B1 | 1018
11 |  | In1(BPF) | Incoming 1 Phase Power Factor (Blue) |  | In1_BPF | 1048
|  |  | Incoming 1 Active Power (Red) | Kilo Watts (kW) | P1_R | 1020 | New
|  |  | Incoming 1 Active Power (Yellow) | Kilo Watts (kW) | P1_B | 1022 | New
|  |  | Incoming 1 Active Power (Blue) | Kilo Watts (kW) | P1_Y | 1024 | New
12 |  | P1 | Incoming 1 Active Power (Total) | Kilo Watts (kW) | P1 | 1026 | New
|  |  | Incoming 1 Reactive Power (Red) | Kilo Volt-Ampere-Reactive (kVAR) | Q1_R | 1028 | New
|  |  | Incoming 1 Reactive Power (Yellow) | Kilo Volt-Ampere-Reactive (kVAR) | Q1_B | 1030 | New
|  |  | Incoming 1 Reactive Power (Blue) | Kilo Volt-Ampere-Reactive (kVAR) | Q1_Y | 1032 | New
13 |  | Q1 | Incoming 1 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | Q1 | 1034 | New
|  |  | Incoming 1 Apparent Power (Red) | Kilo Watts (kW) | S1_R | 1036 | New
|  |  | Incoming 1 Apparent Power (Yellow) | Kilo Watts (kW) | S1_B | 1038 | New
|  |  | Incoming 1 Apparent Power (Blue) | Kilo Watts (kW) | S1_Y | 1040 | New
14 |  | S1 | Incoming 1 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | S1 | 1042 | New
15 |  | In1(BPF) | Incoming 1 Phase Power Factor (Blue) |  | In1_BPF | 1048
16 |  | Epimp1 | Incoming 1 Active Energy (Import) | Kilo Watts-hour (kWh) | Epimp1 | 1054
17 |  | Epexp1 | Incoming 1 Active Energy (Export) | Kilo Watts-hour (kWh) | Epexp1 | 1056
18 |  | Eqimp1 | Incoming 1 Reactive Energy (Import) | Kilo Watts-hour (kWh) | Eqimp1 | 1058
19 |  | Eqexp1 | Incoming 1 Reactive Energy (Export) | Kilo Watts-hour (kWh) | Eqexp1 | 1060
20 | Outgoing | F1(R) | Outgoing 1 Phase Current (Red) | Ampere (A) | F1_R | 1114
21 |  | PF(R1) | Outgoing 1 Phase Power Factor (Red) |  | PF_R1 | 1144
22 |  | F1(Y) | Outgoing 1 Phase Current (Red) | Ampere (A) | F1_Y | 1116
23 |  | PF(Y1) | Outgoing 1 Phase Power Factor (Yellow) |  | PF_Y1 | 1146
24 |  | F1(B) | Outgoing 1 Phase Current (Yellow) | Ampere (A) | F1_B | 1118
25 |  | PF(B1) | Outgoing 1 Phase Power Factor (Blue) |  | PF_B1 | 1148
26 |  | F1(P) | Outgoing 1 Active Power (Total) | Kilo Watts (kW) | F1_P1 | 1126 | New
27 |  | F1(Q) | Outgoing 1 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F1_Q1 | 1134 | New
28 |  | F1(S) | Outgoing 1 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F1_S1 | 1142 | New
29 |  | F1(Epimp) | Outgoing 1 Active Energy (Import) | Kilo Watts-hour (kWh) | F1_Epimp | 1154
30 |  | F1(Epexp) | Outgoing 1 Active Energy (Export) | Kilo Watts-hour (kWh) | F1_Epexp | 1156
31 |  | F1(Eqimp) | Outgoing 1 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F1_Eqimp | 1158
32 |  | F1(Eqexp) | Outgoing 1 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F1_Eqexp | 1160
33 |  | F2(R2) | Outgoing 2 Phase Current (Red) | Ampere (A) | F2_R | 1214
34 |  | PF(R2) | Outgoing 2 Phase Power Factor (Red) |  | PF_R2 | 1244
35 |  | F2(Y) | Outgoing 2 Phase Current (Red) | Ampere (A) | F2_Y | 1216
36 |  | PF(Y2) | Outgoing 2 Phase Power Factor (Yellow) |  | PF_Y2 | 1246
37 |  | F2(B) | Outgoing 2 Phase Current (Yellow) | Ampere (A) | F2_B | 1218
38 |  | PF(B2) | Outgoing 2 Phase Power Factor (Blue) |  | PF_B2 | 1248
39 |  | F2(P) | Outgoing 2 Active Power (Total) | Kilo Watts (kW) | F2_P1 | 1226 | New
40 |  | F2(Q) | Outgoing 2 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F2_Q1 | 1234 | New
41 |  | F2(S) | Outgoing 2 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F2_S1 | 1242 | New
42 |  | F2(Epimp) | Outgoing 2 Active Energy (Import) | Kilo Watts-hour (kWh) | F2_Epimp | 1254
43 |  | F2(Epexp) | Outgoing 2 Active Energy (Export) | Kilo Watts-hour (kWh) | F2_Epexp | 1256
44 |  | F2(Eqimp) | Outgoing 2 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F2_Eqimp | 1258
45 |  | F2(Eqexp) | Outgoing 2 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F2_Eqexp | 1260
46 |  | F3(R) | Outgoing 3 Phase Current (Red) | Ampere (A) | F3_R | 1314
47 |  | PF(R3) | Outgoing 3 Phase Power Factor (Red) |  | PF_R3 | 1344
48 |  | F3(Y) | Outgoing 3 Phase Current (Red) | Ampere (A) | F3_Y | 1316
49 |  | PF(Y3) | Outgoing 3 Phase Power Factor (Yellow) |  | PF_Y3 | 1346
50 |  | F3(B) | Outgoing 3 Phase Current (Yellow) | Ampere (A) | F3_B | 1318
51 |  | PF(B3) | Outgoing 3 Phase Power Factor (Blue) |  | PF_B3 | 1348
52 |  | F3(P) | Outgoing 3 Active Power (Total) | Kilo Watts (kW) | F3_P1 | 1326 | New
53 |  | F3(Q) | Outgoing 3 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F3_Q1 | 1334 | New
54 |  | F3(S) | Outgoing 3 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F3_S1 | 1342 | New
55 |  | F3(Epimp) | Outgoing 3 Active Energy (Import) | Kilo Watts-hour (kWh) | F3_Epimp | 1354
56 |  | F3(Epexp) | Outgoing 3 Active Energy (Export) | Kilo Watts-hour (kWh) | F3_Epexp | 1356
57 |  | F3(Eqimp) | Outgoing 3 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F3_Eqimp | 1358
58 |  | F3(Eqexp) | Outgoing 3 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F3_Eqexp | 1360
59 |  | F4(R) | Outgoing 4 Phase Current (Red) | Ampere (A) | F4_R | 1414
60 |  | PF(R4) | Outgoing 4 Phase Power Factor (Red) |  | PF_R4 | 1444
61 |  | F4(Y) | Outgoing 4 Phase Current (Red) | Ampere (A) | F4_Y | 1416
62 |  | PF(Y4) | Outgoing 4 Phase Power Factor (Yellow) |  | PF_Y4 | 1446
63 |  | F4(B) | Outgoing 4 Phase Current (Yellow) | Ampere (A) | F4_B | 1418
64 |  | PF(B4) | Outgoing 4 Phase Power Factor (Blue) |  | PF_B4 | 1448
65 |  | F4(P) | Outgoing 4 Active Power (Total) | Kilo Watts (kW) | F4_P1 | 1426 | New
66 |  | F4(Q) | Outgoing 4 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F4_Q1 | 1434 | New
67 |  | F4(S) | Outgoing 4 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F4_S1 | 1442 | New
68 |  | F4(Epimp) | Outgoing 4 Active Energy (Import) | Kilo Watts-hour (kWh) | F4_Epimp | 1454
69 |  | F4(Epexp) | Outgoing 4 Active Energy (Export) | Kilo Watts-hour (kWh) | F4_Epexp | 1456
70 |  | F4(Eqimp) | Outgoing 4 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F4_Eqimp | 1458
71 |  | F4(Eqexp) | Outgoing 4 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F4_Eqexp | 1460
72 |  | F5(R) | Outgoing 5 Phase Current (Red) | Ampere (A) | F5_R | 1514
73 |  | PF(R5) | Outgoing 5 Phase Power Factor (Red) |  | PF_R5 | 1544
74 |  | F5(Y) | Outgoing 5 Phase Current (Red) | Ampere (A) | F5_Y | 1516
75 |  | PF(Y5) | Outgoing 5 Phase Power Factor (Yellow) |  | PF_Y5 | 1546
76 |  | F5(B) | Outgoing 5 Phase Current (Yellow) | Ampere (A) | F5_B | 1518
77 |  | PF(B5) | Outgoing 5 Phase Power Factor (Blue) |  | PF_B5 | 1548
78 |  | F5(P) | Outgoing 5 Active Power (Total) | Kilo Watts (kW) | F5_P1 | 1526 | New
79 |  | F5(Q) | Outgoing 5 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F5_Q1 | 1534 | New
80 |  | F5(S) | Outgoing 5 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F5_S1 | 1542 | New
81 |  | F5(Epimp) | Outgoing 5 Active Energy (Import) | Kilo Watts-hour (kWh) | F5_Epimp | 1554
82 |  | F5(Epexp) | Outgoing 5 Active Energy (Export) | Kilo Watts-hour (kWh) | F5_Epexp | 1556
83 |  | F5(Eqimp) | Outgoing 5 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F5_Eqimp | 1558
84 |  | F5(Eqexp) | Outgoing 5 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F5_Eqexp | 1560
85 |  | F6(R) | Outgoing 6 Phase Current (Red) | Ampere (A) | F6_R | 1614
86 |  | PF(R6) | Outgoing 6 Phase Power Factor (Red) |  | PF_R6 | 1644
87 |  | F6(Y) | Outgoing 6 Phase Current (Red) | Ampere (A) | F6_Y | 1616
88 |  | PF(Y6) | Outgoing 6 Phase Power Factor (Yellow) |  | PF_Y6 | 1646
89 |  | F6(B) | Outgoing 6 Phase Current (Yellow) | Ampere (A) | F6_B | 1618
90 |  | PF(B6) | Outgoing 6 Phase Power Factor (Blue) |  | PF_B6 | 1648
91 |  | F6(P) | Outgoing 6 Active Power (Total) | Kilo Watts (kW) | F6_P1 | 1626 | New
92 |  | F6(Q) | Outgoing 6 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F6_Q1 | 1634 | New
93 |  | F6(S) | Outgoing 6 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F6_S1 | 1642 | New
94 |  | F6(Epimp) | Outgoing 6 Active Energy (Import) | Kilo Watts-hour (kWh) | F6_Epimp | 1654
95 |  | F6(Epexp) | Outgoing 6 Active Energy (Export) | Kilo Watts-hour (kWh) | F6_Epexp | 1656
96 |  | F6(Eqimp) | Outgoing 6 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F6_Eqimp | 1658
97 |  | F6(Eqexp) | Outgoing 6 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F6_Eqexp | 1660
98 |  | F7(R) | Outgoing 7 Phase Current (Red) | Ampere (A) | F7_R | 1714
99 |  | PF(R7) | Outgoing 7 Phase Power Factor (Red) |  | PF_R7 | 1744
100 |  | F7(Y) | Outgoing 7 Phase Current (Red) | Ampere (A) | F7_Y | 1716
101 |  | PF(Y7) | Outgoing 7 Phase Power Factor (Yellow) |  | PF_Y7 | 1746
102 |  | F7(B) | Outgoing 7 Phase Current (Yellow) | Ampere (A) | F7_B | 1718
103 |  | PF(B7) | Outgoing 7 Phase Power Factor (Blue) |  | PF_B7 | 1748
104 |  | F7(P) | Outgoing 7 Active Power (Total) | Kilo Watts (kW) | F7_P1 | 1726 | New
105 |  | F7(Q) | Outgoing 7 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F7_Q1 | 1734 | New
106 |  | F7(S) | Outgoing 7 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F7_S1 | 1742 | New
107 |  | F7(Epimp) | Outgoing 7 Active Energy (Import) | Kilo Watts-hour (kWh) | F7_Epimp | 1754
108 |  | F7(Epexp) | Outgoing 7 Active Energy (Export) | Kilo Watts-hour (kWh) | F7_Epexp | 1756
109 |  | F7(Eqimp) | Outgoing 7 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F7_Eqimp | 1758
110 |  | F7(Eqexp) | Outgoing 7 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F7_Eqexp | 1760
111 |  | F8(R) | Outgoing 8 Phase Current (Red) | Ampere (A) | F8_R | 1814
112 |  | PF(R8) | Outgoing 8 Phase Power Factor (Red) |  | PF_R8 | 1844
113 |  | F8(Y) | Outgoing 8 Phase Current (Red) | Ampere (A) | F8_Y | 1816
114 |  | PF(Y8) | Outgoing 8 Phase Power Factor (Yellow) |  | PF_Y8 | 1846
115 |  | F8(B) | Outgoing 8 Phase Current (Yellow) | Ampere (A) | F8_B | 1818
116 |  | PF(B8) | Outgoing 8 Phase Power Factor (Blue) |  | PF_B8 | 1848
117 |  | F8(P) | Outgoing 8 Active Power (Total) | Kilo Watts (kW) | F8_P1 | 1826 | New
118 |  | F8(Q) | Outgoing 8 Reactive Power (Total) | Kilo Volt-Ampere-Reactive (kVAR) | F8_Q1 | 1834 | New
119 |  | F8(S) | Outgoing 8 Apparent Power (Total) | Kilo Volt-Ampere (kVA) | F8_S1 | 1842 | New
120 |  | F8(Epimp) | Outgoing 8 Active Energy (Import) | Kilo Watts-hour (kWh) | F8_Epimp | 1854
121 |  | F8(Epexp) | Outgoing 8 Active Energy (Export) | Kilo Watts-hour (kWh) | F8_Epexp | 1856
122 |  | F8(Eqimp) | Outgoing 8 Reactive Energy (Import) | Kilovolt-amperes-reactive hours (kVARh) | F8_Eqimp | 1858
123 |  | F8(Eqexp) | Outgoing 8 Reactive Energy (Export) | Kilovolt-amperes-reactive hours (kVARh) | F8_Eqexp | 1860
Note: No positive or negative sign for Import or Export

## Sheet1
|  | 1002 : { id: 'V_R', value: null, datetime: null }, 1014 : { id: 'In1_R1', value: null, datetime: null }, 1044 : { id: 'In1_RPF', value: null, datetime: null }, 1004 : { id: 'V_Y', value: null, datetime: null }, 1016 : { id: 'In1_Y1', value: null, datetime: null }, 1046 : { id: 'In1_YPF', value: null, datetime: null }, 1006 : { id: 'V_B', value: null, datetime: null }, 1018 : { id: 'In1_B1', value: null, datetime: null }, 1048 : { id: 'In1_BPF', value: null, datetime: null }, 1020 : { id: 'P1_R', value: null, datetime: null }, 1022 : { id: 'P1_B', value: null, datetime: null }, 1024 : { id: 'P1_Y', value: null, datetime: null }, 1026 : { id: 'P1', value: null, datetime: null }, 1028 : { id: 'Q1_R', value: null, datetime: null }, 1030 : { id: 'Q1_B', value: null, datetime: null }, 1032 : { id: 'Q1_Y', value: null, datetime: null }, 1034 : { id: 'Q1', value: null, datetime: null }, 1036 : { id: 'S1_R', value: null, datetime: null }, 1038 : { id: 'S1_B', value: null, datetime: null }, 1040 : { id: 'S1_Y', value: null, datetime: null }, 1042 : { id: 'S1', value: null, datetime: null }, 1054 : { id: 'Epimp1', value: null, datetime: null }, 1056 : { id: 'Epexp1', value: null, datetime: null }, 1058 : { id: 'Eqimp1', value: null, datetime: null }, 1060 : { id: 'Eqexp1', value: null, datetime: null }, 1114 : { id: 'F1_R', value: null, datetime: null }, 1144 : { id: 'PF_R1', value: null, datetime: null }, 1116 : { id: 'F1_Y', value: null, datetime: null }, 1146 : { id: 'PF_Y1', value: null, datetime: null }, 1118 : { id: 'F1_B', value: null, datetime: null }, 1148 : { id: 'PF_B1', value: null, datetime: null }, 1126 : { id: 'F1_P', value: null, datetime: null }, 1134 : { id: 'F1_Q', value: null, datetime: null }, 1142 : { id: 'F1_S', value: null, datetime: null }, 1154 : { id: 'F1_Epimp', value: null, datetime: null }, 1156 : { id: 'F1_Epexp', value: null, datetime: null }, 1158 : { id: 'F1_Eqimp', value: null, datetime: null }, 1160 : { id: 'F1_Eqexp', value: null, datetime: null }, 1214 : { id: 'F2_R', value: null, datetime: null }, 1244 : { id: 'PF_R2', value: null, datetime: null }, 1216 : { id: 'F2_Y', value: null, datetime: null }, 1246 : { id: 'PF_Y2', value: null, datetime: null }, 1218 : { id: 'F2_B', value: null, datetime: null }, 1248 : { id: 'PF_B2', value: null, datetime: null }, 1226 : { id: 'F2_P', value: null, datetime: null }, 1234 : { id: 'F2_Q', value: null, datetime: null }, 1242 : { id: 'F2_S', value: null, datetime: null }, 1254 : { id: 'F2_Epimp', value: null, datetime: null }, 1256 : { id: 'F2_Epexp', value: null, datetime: null }, 1258 : { id: 'F2_Eqimp', value: null, datetime: null }, 1260 : { id: 'F2_Eqexp', value: null, datetime: null }, 1314 : { id: 'F3_R', value: null, datetime: null }, 1344 : { id: 'PF_R3', value: null, datetime: null }, 1316 : { id: 'F3_Y', value: null, datetime: null }, 1346 : { id: 'PF_Y3', value: null, datetime: null }, 1318 : { id: 'F3_B', value: null, datetime: null }, 1348 : { id: 'PF_B3', value: null, datetime: null }, 1326 : { id: 'F3_P', value: null, datetime: null }, 1334 : { id: 'F3_Q', value: null, datetime: null }, 1342 : { id: 'F3_S', value: null, datetime: null }, 1354 : { id: 'F3_Epimp', value: null, datetime: null }, 1356 : { id: 'F3_Epexp', value: null, datetime: null }, 1358 : { id: 'F3_Eqimp', value: null, datetime: null }, 1360 : { id: 'F3_Eqexp', value: null, datetime: null }, 1414 : { id: 'F4_R', value: null, datetime: null }, 1444 : { id: 'PF_R4', value: null, datetime: null }, 1416 : { id: 'F4_Y', value: null, datetime: null }, 1446 : { id: 'PF_Y4', value: null, datetime: null }, 1418 : { id: 'F4_B', value: null, datetime: null }, 1448 : { id: 'PF_B4', value: null, datetime: null }, 1426 : { id: 'F4_P', value: null, datetime: null }, 1434 : { id: 'F4_Q', value: null, datetime: null }, 1442 : { id: 'F4_S', value: null, datetime: null }, 1454 : { id: 'F4_Epimp', value: null, datetime: null }, 1456 : { id: 'F4_Epexp', value: null, datetime: null }, 1458 : { id: 'F4_Eqimp', value: null, datetime: null }, 1460 : { id: 'F4_Eqexp', value: null, datetime: null }, 1514 : { id: 'F5_R', value: null, datetime: null }, 1544 : { id: 'PF_R5', value: null, datetime: null }, 1516 : { id: 'F5_Y', value: null, datetime: null }, 1546 : { id: 'PF_Y5', value: null, datetime: null }, 1518 : { id: 'F5_B', value: null, datetime: null }, 1548 : { id: 'PF_B5', value: null, datetime: null }, 1526 : { id: 'F5_P', value: null, datetime: null }, 1534 : { id: 'F5_Q', value: null, datetime: null }, 1542 : { id: 'F5_S', value: null, datetime: null }, 1554 : { id: 'F5_Epimp', value: null, datetime: null }, 1556 : { id: 'F5_Epexp', value: null, datetime: null }, 1558 : { id: 'F5_Eqimp', value: null, datetime: null }, 1560 : { id: 'F5_Eqexp', value: null, datetime: null }, 1614 : { id: 'F6_R', value: null, datetime: null }, 1644 : { id: 'PF_R6', value: null, datetime: null }, 1616 : { id: 'F6_Y', value: null, datetime: null }, 1646 : { id: 'PF_Y6', value: null, datetime: null }, 1618 : { id: 'F6_B', value: null, datetime: null }, 1648 : { id: 'PF_B6', value: null, datetime: null }, 1626 : { id: 'F6_P', value: null, datetime: null }, 1634 : { id: 'F6_Q', value: null, datetime: null }, 1642 : { id: 'F6_S', value: null, datetime: null }, 1654 : { id: 'F6_Epimp', value: null, datetime: null }, 1656 : { id: 'F6_Epexp', value: null, datetime: null }, 1658 : { id: 'F6_Eqimp', value: null, datetime: null }, 1660 : { id: 'F6_Eqexp', value: null, datetime: null }, 1714 : { id: 'F7_R', value: null, datetime: null }, 1744 : { id: 'PF_R7', value: null, datetime: null }, 1716 : { id: 'F7_Y', value: null, datetime: null }, 1746 : { id: 'PF_Y7', value: null, datetime: null }, 1718 : { id: 'F7_B', value: null, datetime: null }, 1748 : { id: 'PF_B7', value: null, datetime: null }, 1726 : { id: 'F7_P', value: null, datetime: null }, 1734 : { id: 'F7_Q', value: null, datetime: null }, 1742 : { id: 'F7_S', value: null, datetime: null }, 1754 : { id: 'F7_Epimp', value: null, datetime: null }, 1756 : { id: 'F7_Epexp', value: null, datetime: null }, 1758 : { id: 'F7_Eqimp', value: null, datetime: null }, 1760 : { id: 'F7_Eqexp', value: null, datetime: null }, 1814 : { id: 'F8_R', value: null, datetime: null }, 1844 : { id: 'PF_R8', value: null, datetime: null }, 1816 : { id: 'F8_Y', value: null, datetime: null }, 1846 : { id: 'PF_Y8', value: null, datetime: null }, 1818 : { id: 'F8_B', value: null, datetime: null }, 1848 : { id: 'PF_B8', value: null, datetime: null }, 1826 : { id: 'F8_P', value: null, datetime: null }, 1834 : { id: 'F8_Q', value: null, datetime: null }, 1842 : { id: 'F8_S', value: null, datetime: null }, 1854 : { id: 'F8_Epimp', value: null, datetime: null }, 1856 : { id: 'F8_Epexp', value: null, datetime: null }, 1858 : { id: 'F8_Eqimp', value: null, datetime: null }, 1860 : { id: 'F8_Eqexp', value: null, datetime: null }, | V_R In1_R1 In1_RPF V_Y In1_Y1 In1_YPF V_B In1_B1 In1_BPF P1_R P1_B P1_Y P1 Q1_R Q1_B Q1_Y Q1 S1_R S1_B S1_Y S1 Epimp1 Epexp1 Eqimp1 Eqexp1 F1_R PF_R1 F1_Y PF_Y1 F1_B PF_B1 F1_P F1_Q F1_S F1_Epimp F1_Epexp F1_Eqimp F1_Eqexp F2_R2 PF_R2 F2_Y PF_Y2 F2_B PF_B2 F2_P F2_Q F2_S F2_Epimp F2_Epexp F2_Eqimp F2_Eqexp F3_R PF_R3 F3_Y PF_Y3 F3_B PF_B3 F3_P F3_Q F3_S F3_Epimp F3_Epexp F3_Eqimp F3_Eqexp F4_R PF_R4 F4_Y PF_Y4 F4_B PF_B4 F4_P F4_Q F4_S F4_Epimp F4_Epexp F4_Eqimp F4_Eqexp F5_R PF_R5 F5_Y PF_Y5 F5_B PF_B5 F5_P F5_Q F5_S F5_Epimp F5_Epexp F5_Eqimp F5_Eqexp F6_R PF_R6 F6_Y PF_Y6 F6_B PF_B6 F6_P F6_Q F6_S F6_Epimp F6_Epexp F6_Eqimp F6_Eqexp F7_R PF_R7 F7_Y PF_Y7 F7_B PF_B7 F7_P F7_Q F7_S F7_Epimp F7_Epexp F7_Eqimp F7_Eqexp F8_R PF_R8 F8_Y PF_Y8 F8_B PF_B8 F8_P F8_Q F8_S F8_Epimp F8_Epexp F8_Eqimp F8_Eqexp | `V_R`, `In1_R1`, `In1_RPF`, `V_Y`, `In1_Y1`, `In1_YPF`, `V_B`, `In1_B1`, `In1_BPF`, `P1_R`, `P1_B`, `P1_Y`, `P1`, `Q1_R`, `Q1_B`, `Q1_Y`, `Q1`, `S1_R`, `S1_B`, `S1_Y`, `S1`, `Epimp1`, `Epexp1`, `Eqimp1`, `Eqexp1`, `F1_R`, `PF_R1`, `F1_Y`, `PF_Y1`, `F1_B`, `PF_B1`, `F1_P`, `F1_Q`, `F1_S`, `F1_Epimp`, `F1_Epexp`, `F1_Eqimp`, `F1_Eqexp`, `F2_R`, `PF_R2`, `F2_Y`, `PF_Y2`, `F2_B`, `PF_B2`, `F2_P`, `F2_Q`, `F2_S`, `F2_Epimp`, `F2_Epexp`, `F2_Eqimp`, `F2_Eqexp`, `F3_R`, `PF_R3`, `F3_Y`, `PF_Y3`, `F3_B`, `PF_B3`, `F3_P`, `F3_Q`, `F3_S`, `F3_Epimp`, `F3_Epexp`, `F3_Eqimp`, `F3_Eqexp`, `F4_R`, `PF_R4`, `F4_Y`, `PF_Y4`, `F4_B`, `PF_B4`, `F4_P`, `F4_Q`, `F4_S`, `F4_Epimp`, `F4_Epexp`, `F4_Eqimp`, `F4_Eqexp`, `F5_R`, `PF_R5`, `F5_Y`, `PF_Y5`, `F5_B`, `PF_B5`, `F5_P`, `F5_Q`, `F5_S`, `F5_Epimp`, `F5_Epexp`, `F5_Eqimp`, `F5_Eqexp`, `F6_R`, `PF_R6`, `F6_Y`, `PF_Y6`, `F6_B`, `PF_B6`, `F6_P`, `F6_Q`, `F6_S`, `F6_Epimp`, `F6_Epexp`, `F6_Eqimp`, `F6_Eqexp`, `F7_R`, `PF_R7`, `F7_Y`, `PF_Y7`, `F7_B`, `PF_B7`, `F7_P`, `F7_Q`, `F7_S`, `F7_Epimp`, `F7_Epexp`, `F7_Eqimp`, `F7_Eqexp`, `F8_R`, `PF_R8`, `F8_Y`, `PF_Y8`, `F8_B`, `PF_B8`, `F8_P`, `F8_Q`, `F8_S`, `F8_Epimp`, `F8_Epexp`, `F8_Eqimp`, `F8_Eqexp`,
V_R | 1002 | 1002 : { id: 'V_R', value: null, datetime: null }, | V_R | `V_R`,
In1_R1 | 1014 | 1014 : { id: 'In1_R1', value: null, datetime: null }, | In1_R1 | `In1_R1`,
In1_RPF | 1044 | 1044 : { id: 'In1_RPF', value: null, datetime: null }, | In1_RPF | `In1_RPF`,
V_Y | 1004 | 1004 : { id: 'V_Y', value: null, datetime: null }, | V_Y | `V_Y`,
In1_Y1 | 1016 | 1016 : { id: 'In1_Y1', value: null, datetime: null }, | In1_Y1 | `In1_Y1`,
In1_YPF | 1046 | 1046 : { id: 'In1_YPF', value: null, datetime: null }, | In1_YPF | `In1_YPF`,
V_B | 1006 | 1006 : { id: 'V_B', value: null, datetime: null }, | V_B | `V_B`,
In1_B1 | 1018 | 1018 : { id: 'In1_B1', value: null, datetime: null }, | In1_B1 | `In1_B1`,
In1_BPF | 1048 | 1048 : { id: 'In1_BPF', value: null, datetime: null }, | In1_BPF | `In1_BPF`,
P1_R | 1020 | 1020 : { id: 'P1_R', value: null, datetime: null }, | P1_R | `P1_R`,
P1_B | 1022 | 1022 : { id: 'P1_B', value: null, datetime: null }, | P1_B | `P1_B`,
P1_Y | 1024 | 1024 : { id: 'P1_Y', value: null, datetime: null }, | P1_Y | `P1_Y`,
P1 | 1026 | 1026 : { id: 'P1', value: null, datetime: null }, | P1 | `P1`,
Q1_R | 1028 | 1028 : { id: 'Q1_R', value: null, datetime: null }, | Q1_R | `Q1_R`,
Q1_B | 1030 | 1030 : { id: 'Q1_B', value: null, datetime: null }, | Q1_B | `Q1_B`,
Q1_Y | 1032 | 1032 : { id: 'Q1_Y', value: null, datetime: null }, | Q1_Y | `Q1_Y`,
Q1 | 1034 | 1034 : { id: 'Q1', value: null, datetime: null }, | Q1 | `Q1`,
S1_R | 1036 | 1036 : { id: 'S1_R', value: null, datetime: null }, | S1_R | `S1_R`,
S1_B | 1038 | 1038 : { id: 'S1_B', value: null, datetime: null }, | S1_B | `S1_B`,
S1_Y | 1040 | 1040 : { id: 'S1_Y', value: null, datetime: null }, | S1_Y | `S1_Y`,
S1 | 1042 | 1042 : { id: 'S1', value: null, datetime: null }, | S1 | `S1`,
Epimp1 | 1054 | 1054 : { id: 'Epimp1', value: null, datetime: null }, | Epimp1 | `Epimp1`,
Epexp1 | 1056 | 1056 : { id: 'Epexp1', value: null, datetime: null }, | Epexp1 | `Epexp1`,
Eqimp1 | 1058 | 1058 : { id: 'Eqimp1', value: null, datetime: null }, | Eqimp1 | `Eqimp1`,
Eqexp1 | 1060 | 1060 : { id: 'Eqexp1', value: null, datetime: null }, | Eqexp1 | `Eqexp1`,
F1_R | 1114 | 1114 : { id: 'F1_R', value: null, datetime: null }, | F1_R | `F1_R`,
PF_R1 | 1144 | 1144 : { id: 'PF_R1', value: null, datetime: null }, | PF_R1 | `PF_R1`,
F1_Y | 1116 | 1116 : { id: 'F1_Y', value: null, datetime: null }, | F1_Y | `F1_Y`,
PF_Y1 | 1146 | 1146 : { id: 'PF_Y1', value: null, datetime: null }, | PF_Y1 | `PF_Y1`,
F1_B | 1118 | 1118 : { id: 'F1_B', value: null, datetime: null }, | F1_B | `F1_B`,
PF_B1 | 1148 | 1148 : { id: 'PF_B1', value: null, datetime: null }, | PF_B1 | `PF_B1`,
F1_P | 1126 | 1126 : { id: 'F1_P', value: null, datetime: null }, | F1_P | `F1_P`,
F1_Q | 1134 | 1134 : { id: 'F1_Q', value: null, datetime: null }, | F1_Q | `F1_Q`,
F1_S | 1142 | 1142 : { id: 'F1_S', value: null, datetime: null }, | F1_S | `F1_S`,
F1_Epimp | 1154 | 1154 : { id: 'F1_Epimp', value: null, datetime: null }, | F1_Epimp | `F1_Epimp`,
F1_Epexp | 1156 | 1156 : { id: 'F1_Epexp', value: null, datetime: null }, | F1_Epexp | `F1_Epexp`,
F1_Eqimp | 1158 | 1158 : { id: 'F1_Eqimp', value: null, datetime: null }, | F1_Eqimp | `F1_Eqimp`,
F1_Eqexp | 1160 | 1160 : { id: 'F1_Eqexp', value: null, datetime: null }, | F1_Eqexp | `F1_Eqexp`,
F2_R | 1214 | 1214 : { id: 'F2_R', value: null, datetime: null }, | F2_R2 | `F2_R`,
PF_R2 | 1244 | 1244 : { id: 'PF_R2', value: null, datetime: null }, | PF_R2 | `PF_R2`,
F2_Y | 1216 | 1216 : { id: 'F2_Y', value: null, datetime: null }, | F2_Y | `F2_Y`,
PF_Y2 | 1246 | 1246 : { id: 'PF_Y2', value: null, datetime: null }, | PF_Y2 | `PF_Y2`,
F2_B | 1218 | 1218 : { id: 'F2_B', value: null, datetime: null }, | F2_B | `F2_B`,
PF_B2 | 1248 | 1248 : { id: 'PF_B2', value: null, datetime: null }, | PF_B2 | `PF_B2`,
F2_P | 1226 | 1226 : { id: 'F2_P', value: null, datetime: null }, | F2_P | `F2_P`,
F2_Q | 1234 | 1234 : { id: 'F2_Q', value: null, datetime: null }, | F2_Q | `F2_Q`,
F2_S | 1242 | 1242 : { id: 'F2_S', value: null, datetime: null }, | F2_S | `F2_S`,
F2_Epimp | 1254 | 1254 : { id: 'F2_Epimp', value: null, datetime: null }, | F2_Epimp | `F2_Epimp`,
F2_Epexp | 1256 | 1256 : { id: 'F2_Epexp', value: null, datetime: null }, | F2_Epexp | `F2_Epexp`,
F2_Eqimp | 1258 | 1258 : { id: 'F2_Eqimp', value: null, datetime: null }, | F2_Eqimp | `F2_Eqimp`,
F2_Eqexp | 1260 | 1260 : { id: 'F2_Eqexp', value: null, datetime: null }, | F2_Eqexp | `F2_Eqexp`,
F3_R | 1314 | 1314 : { id: 'F3_R', value: null, datetime: null }, | F3_R | `F3_R`,
PF_R3 | 1344 | 1344 : { id: 'PF_R3', value: null, datetime: null }, | PF_R3 | `PF_R3`,
F3_Y | 1316 | 1316 : { id: 'F3_Y', value: null, datetime: null }, | F3_Y | `F3_Y`,
PF_Y3 | 1346 | 1346 : { id: 'PF_Y3', value: null, datetime: null }, | PF_Y3 | `PF_Y3`,
F3_B | 1318 | 1318 : { id: 'F3_B', value: null, datetime: null }, | F3_B | `F3_B`,
PF_B3 | 1348 | 1348 : { id: 'PF_B3', value: null, datetime: null }, | PF_B3 | `PF_B3`,
F3_P | 1326 | 1326 : { id: 'F3_P', value: null, datetime: null }, | F3_P | `F3_P`,
F3_Q | 1334 | 1334 : { id: 'F3_Q', value: null, datetime: null }, | F3_Q | `F3_Q`,
F3_S | 1342 | 1342 : { id: 'F3_S', value: null, datetime: null }, | F3_S | `F3_S`,
F3_Epimp | 1354 | 1354 : { id: 'F3_Epimp', value: null, datetime: null }, | F3_Epimp | `F3_Epimp`,
F3_Epexp | 1356 | 1356 : { id: 'F3_Epexp', value: null, datetime: null }, | F3_Epexp | `F3_Epexp`,
F3_Eqimp | 1358 | 1358 : { id: 'F3_Eqimp', value: null, datetime: null }, | F3_Eqimp | `F3_Eqimp`,
F3_Eqexp | 1360 | 1360 : { id: 'F3_Eqexp', value: null, datetime: null }, | F3_Eqexp | `F3_Eqexp`,
F4_R | 1414 | 1414 : { id: 'F4_R', value: null, datetime: null }, | F4_R | `F4_R`,
PF_R4 | 1444 | 1444 : { id: 'PF_R4', value: null, datetime: null }, | PF_R4 | `PF_R4`,
F4_Y | 1416 | 1416 : { id: 'F4_Y', value: null, datetime: null }, | F4_Y | `F4_Y`,
PF_Y4 | 1446 | 1446 : { id: 'PF_Y4', value: null, datetime: null }, | PF_Y4 | `PF_Y4`,
F4_B | 1418 | 1418 : { id: 'F4_B', value: null, datetime: null }, | F4_B | `F4_B`,
PF_B4 | 1448 | 1448 : { id: 'PF_B4', value: null, datetime: null }, | PF_B4 | `PF_B4`,
F4_P | 1426 | 1426 : { id: 'F4_P', value: null, datetime: null }, | F4_P | `F4_P`,
F4_Q | 1434 | 1434 : { id: 'F4_Q', value: null, datetime: null }, | F4_Q | `F4_Q`,
F4_S | 1442 | 1442 : { id: 'F4_S', value: null, datetime: null }, | F4_S | `F4_S`,
F4_Epimp | 1454 | 1454 : { id: 'F4_Epimp', value: null, datetime: null }, | F4_Epimp | `F4_Epimp`,
F4_Epexp | 1456 | 1456 : { id: 'F4_Epexp', value: null, datetime: null }, | F4_Epexp | `F4_Epexp`,
F4_Eqimp | 1458 | 1458 : { id: 'F4_Eqimp', value: null, datetime: null }, | F4_Eqimp | `F4_Eqimp`,
F4_Eqexp | 1460 | 1460 : { id: 'F4_Eqexp', value: null, datetime: null }, | F4_Eqexp | `F4_Eqexp`,
F5_R | 1514 | 1514 : { id: 'F5_R', value: null, datetime: null }, | F5_R | `F5_R`,
PF_R5 | 1544 | 1544 : { id: 'PF_R5', value: null, datetime: null }, | PF_R5 | `PF_R5`,
F5_Y | 1516 | 1516 : { id: 'F5_Y', value: null, datetime: null }, | F5_Y | `F5_Y`,
PF_Y5 | 1546 | 1546 : { id: 'PF_Y5', value: null, datetime: null }, | PF_Y5 | `PF_Y5`,
F5_B | 1518 | 1518 : { id: 'F5_B', value: null, datetime: null }, | F5_B | `F5_B`,
PF_B5 | 1548 | 1548 : { id: 'PF_B5', value: null, datetime: null }, | PF_B5 | `PF_B5`,
F5_P | 1526 | 1526 : { id: 'F5_P', value: null, datetime: null }, | F5_P | `F5_P`,
F5_Q | 1534 | 1534 : { id: 'F5_Q', value: null, datetime: null }, | F5_Q | `F5_Q`,
F5_S | 1542 | 1542 : { id: 'F5_S', value: null, datetime: null }, | F5_S | `F5_S`,
F5_Epimp | 1554 | 1554 : { id: 'F5_Epimp', value: null, datetime: null }, | F5_Epimp | `F5_Epimp`,
F5_Epexp | 1556 | 1556 : { id: 'F5_Epexp', value: null, datetime: null }, | F5_Epexp | `F5_Epexp`,
F5_Eqimp | 1558 | 1558 : { id: 'F5_Eqimp', value: null, datetime: null }, | F5_Eqimp | `F5_Eqimp`,
F5_Eqexp | 1560 | 1560 : { id: 'F5_Eqexp', value: null, datetime: null }, | F5_Eqexp | `F5_Eqexp`,
F6_R | 1614 | 1614 : { id: 'F6_R', value: null, datetime: null }, | F6_R | `F6_R`,
PF_R6 | 1644 | 1644 : { id: 'PF_R6', value: null, datetime: null }, | PF_R6 | `PF_R6`,
F6_Y | 1616 | 1616 : { id: 'F6_Y', value: null, datetime: null }, | F6_Y | `F6_Y`,
PF_Y6 | 1646 | 1646 : { id: 'PF_Y6', value: null, datetime: null }, | PF_Y6 | `PF_Y6`,
F6_B | 1618 | 1618 : { id: 'F6_B', value: null, datetime: null }, | F6_B | `F6_B`,
PF_B6 | 1648 | 1648 : { id: 'PF_B6', value: null, datetime: null }, | PF_B6 | `PF_B6`,
F6_P | 1626 | 1626 : { id: 'F6_P', value: null, datetime: null }, | F6_P | `F6_P`,
F6_Q | 1634 | 1634 : { id: 'F6_Q', value: null, datetime: null }, | F6_Q | `F6_Q`,
F6_S | 1642 | 1642 : { id: 'F6_S', value: null, datetime: null }, | F6_S | `F6_S`,
F6_Epimp | 1654 | 1654 : { id: 'F6_Epimp', value: null, datetime: null }, | F6_Epimp | `F6_Epimp`,
F6_Epexp | 1656 | 1656 : { id: 'F6_Epexp', value: null, datetime: null }, | F6_Epexp | `F6_Epexp`,
F6_Eqimp | 1658 | 1658 : { id: 'F6_Eqimp', value: null, datetime: null }, | F6_Eqimp | `F6_Eqimp`,
F6_Eqexp | 1660 | 1660 : { id: 'F6_Eqexp', value: null, datetime: null }, | F6_Eqexp | `F6_Eqexp`,
F7_R | 1714 | 1714 : { id: 'F7_R', value: null, datetime: null }, | F7_R | `F7_R`,
PF_R7 | 1744 | 1744 : { id: 'PF_R7', value: null, datetime: null }, | PF_R7 | `PF_R7`,
F7_Y | 1716 | 1716 : { id: 'F7_Y', value: null, datetime: null }, | F7_Y | `F7_Y`,
PF_Y7 | 1746 | 1746 : { id: 'PF_Y7', value: null, datetime: null }, | PF_Y7 | `PF_Y7`,
F7_B | 1718 | 1718 : { id: 'F7_B', value: null, datetime: null }, | F7_B | `F7_B`,
PF_B7 | 1748 | 1748 : { id: 'PF_B7', value: null, datetime: null }, | PF_B7 | `PF_B7`,
F7_P | 1726 | 1726 : { id: 'F7_P', value: null, datetime: null }, | F7_P | `F7_P`,
F7_Q | 1734 | 1734 : { id: 'F7_Q', value: null, datetime: null }, | F7_Q | `F7_Q`,
F7_S | 1742 | 1742 : { id: 'F7_S', value: null, datetime: null }, | F7_S | `F7_S`,
F7_Epimp | 1754 | 1754 : { id: 'F7_Epimp', value: null, datetime: null }, | F7_Epimp | `F7_Epimp`,
F7_Epexp | 1756 | 1756 : { id: 'F7_Epexp', value: null, datetime: null }, | F7_Epexp | `F7_Epexp`,
F7_Eqimp | 1758 | 1758 : { id: 'F7_Eqimp', value: null, datetime: null }, | F7_Eqimp | `F7_Eqimp`,
F7_Eqexp | 1760 | 1760 : { id: 'F7_Eqexp', value: null, datetime: null }, | F7_Eqexp | `F7_Eqexp`,
F8_R | 1814 | 1814 : { id: 'F8_R', value: null, datetime: null }, | F8_R | `F8_R`,
PF_R8 | 1844 | 1844 : { id: 'PF_R8', value: null, datetime: null }, | PF_R8 | `PF_R8`,
F8_Y | 1816 | 1816 : { id: 'F8_Y', value: null, datetime: null }, | F8_Y | `F8_Y`,
PF_Y8 | 1846 | 1846 : { id: 'PF_Y8', value: null, datetime: null }, | PF_Y8 | `PF_Y8`,
F8_B | 1818 | 1818 : { id: 'F8_B', value: null, datetime: null }, | F8_B | `F8_B`,
PF_B8 | 1848 | 1848 : { id: 'PF_B8', value: null, datetime: null }, | PF_B8 | `PF_B8`,
F8_P | 1826 | 1826 : { id: 'F8_P', value: null, datetime: null }, | F8_P | `F8_P`,
F8_Q | 1834 | 1834 : { id: 'F8_Q', value: null, datetime: null }, | F8_Q | `F8_Q`,
F8_S | 1842 | 1842 : { id: 'F8_S', value: null, datetime: null }, | F8_S | `F8_S`,
F8_Epimp | 1854 | 1854 : { id: 'F8_Epimp', value: null, datetime: null }, | F8_Epimp | `F8_Epimp`,
F8_Epexp | 1856 | 1856 : { id: 'F8_Epexp', value: null, datetime: null }, | F8_Epexp | `F8_Epexp`,
F8_Eqimp | 1858 | 1858 : { id: 'F8_Eqimp', value: null, datetime: null }, | F8_Eqimp | `F8_Eqimp`,
F8_Eqexp | 1860 | 1860 : { id: 'F8_Eqexp', value: null, datetime: null }, | F8_Eqexp | `F8_Eqexp`,